SECTION 4 - WATER SPECIFICATIONS

4.1	General

A. Scope of Work

- Supply all labor, equipment, materials and incidentals necessary to install and test all water supply piping and appurtenances as specified.

- Work shall include, but not be limited to all excavation, backfilling, sheeting, slope protection, drainage, concrete work, rip-rap, grading, and all other work necessary to complete the construction, installation, and testing of the pipe.

B. Qualifications

- The pipe and fittings shall be designed, constructed, and installed in accordance with these Specifications as applicable.

C. Submittals and Testing

- The Contractor shall submit, to the City of Roswell, prior to start of construction, a list of materials to be furnished.

- Submit shop drawings to the City of Roswell.

D. Inspection

- All pipe and fittings to be installed may be inspected by the City of Roswell at the site of manufacturer for compliance with these Specifications.

E. Connection to Work by Others or Existing Lines

- Contractor shall expose existing lines or lines installed by others to which new piping will connect and confirm or determine end connection type, pipe material, and pipe diameter and shall furnish and install appropriate piping and make proper connections.

4.2	Products

A. General

- All materials used shall be new.

- All materials shall be of standard manufactured design that the manufacturer recommends for the service intended in accordance with AWWA or ASTM Standard Specifications.

- All pipe and appurtenances shall be of the size shown on the Drawings and all equipment of the same type shall be from one manufacturer.

B. Water Line Pipe Materials

- Water line pipe materials shall be as follows.

- Water lines 4-inches in diameter and larger shall be ductile iron pipe.

- Water lines smaller than 4-inches in diameter shall be Schedule 80 polyvinyl chloride (PVC) pipe.

- Service lines ¾-inch diameter to 2-inch diameter shall be copper tubing or copper pipe.

C. Ductile Iron Pipe and Fittings

- Ductile iron pipe shall meet the following requirements.

- Ductile iron pipe shall be minimum Pressure Class 350 and shall conform to ANSI/AWWA C150/A21.50 and ANSI/AWWA C151/A21.51.

- Ductile iron used to manufacture ductile iron pipe shall have a minimum tensile strength of 60,000 PSI, minimum yield strength of 42,000 PSI, and minimum elongation of 10 percent.

- Joints for buried pipe shall be push-on joints conforming to ANSI/AWWA C111/A21.11.

- Joints for above grade (non-buried) pipe shall be flanged joints conforming to ANSI/AWWA C115/A21.15.

- Gaskets for standard push-on joints shall be plain rubber gaskets conforming to ANSI/AWWA C111/A21.11.

- Gaskets for restrained push-on joints shall be plain rubber gasket with restraining teeth conforming to ANSI/AWWA C111/A21.11.

- Gaskets for flanged joints shall be full face, 1/8” thick, plain rubber gaskets with dimensions conforming to ANSI/AWWA C115/A21.15.

- The interior of ductile iron pipe shall be coated with standard thickness cement-mortar in accordance with ANSI/AWWA C104/A21.4.

- The exterior of buried ductile iron pipe shall have an asphaltic coating in accordance with ANSI/AWWA C151/A21.51.

- The exterior of ductile iron pipe installed above the ground surface shall have a 1-mil, manufacturer applied, universal primer capable of accepting an epoxy coating.

- Hardware for flanged joints shall be heavy hex type, low carbon steel, zinc plated bolts conforming to ASTM A307, Grade B; heavy hex type, low carbon steel, zinc plated nuts conforming to ASTM A563, Grade B; and low carbon steel, zinc plated SAE flat washers conforming to ASTM F844.

- Ductile iron fittings shall meet the following requirements.

- Standard ductile iron fittings shall conform to ANSI/AWWA C110/A21.10.

- Compact ductile iron fittings shall conform to ANSI/AWWA C153/A21.53.

- Ductile iron used to manufacture ductile iron fittings shall have a minimum tensile strength of 70,000 PSI, minimum yield strength of 50,000 PSI, and minimum elongation of 5 percent.

- Joints for buried fittings shall be mechanical joints conforming to ANSI/AWWA C111/A21.11.

- Joints for above grade (non-buried) fittings shall be flanged joints conforming to ANSI/AWWA C110/A21.10.

- Mechanical joints that require restraining shall be restrained with wedge type mechanical joint retainer glands for ductile iron pipe.  Retainer gland dimensions shall conform to ANSI/AWWA C111/A21.11 or ANSI/AWWA C153/A21.53.

- Gaskets for mechanical joints shall be plain rubber gasket conforming to ANSI/AWWA C111/A21.11.

- Gaskets for flanged joints shall be full face, 1/8” thick, plain rubber gasket with dimensions conforming to ANSI/AWWA C115/A21.15.

- The interior of ductile iron fittings shall be coated with double thickness cement-mortar in accordance with ANSI/AWWA C104/A21.4.

- The exterior of buried ductile iron fittings shall have an asphaltic coating in accordance with ANSI/AWWA C151/A21.51.

- The exterior of ductile iron fittings installed above the ground surface shall have a 1-mil, manufacturer applied, universal primer capable of accepting an epoxy coating.

- Hardware for mechanical joints shall be low carbon steel, zinc plated tee-head bolts in accordance with ANSI/AWWA C111/A21.11 and heavy hex type, low carbon steel, zinc plated nuts conforming to ASTM A563.

- Hardware for flanged joints shall be heavy hex type, low carbon steel, zinc plated bolts conforming to ASTM A307, Grade B; heavy hex type, low carbon steel, zinc plated nuts conforming to ASTM A563, Grade B; and low carbon steel, zinc plated SAE flat washers conforming to ASTM F844.

- The pressure rating and manufacture date shall be shown on each joint of pipe and each fitting.

- Every precaution shall be taken to prevent damage to the lining.  If the lining is damaged or found to be faulty at the delivery site, the damaged or unsatisfactory portions shall be replaced or repaired with a lining in conformance with the recommendations of the manufacturer.  All repairs shall be as smooth as practical and may not project into the waterway.

- Acceptable Manufacturers

- American Cast Iron Pipe Company

- U.S. Pipe and Foundry Company

- City of Roswell Approved Equal

D. Schedule 80 PVC Pipe and Fittings

- Schedule 80 PVC pipe shall meet the following requirements.

- Schedule 80 PVC pipe shall conform to ASTM D1785.

- PVC shall meet the requirement of Cell Classification 12454 in conformance with ASTM D1784.

- Joints shall conform to ASTM D2672.

- Tracer wire shall be installed on all PVC pipe.  Tracer wire shall meet the following requirements.

- Direct burial #14 AWG solid, soft drawn, high strength copper clad steel wire.

- 30 volt rating.

- 30-mil high molecular weight, high density, polyethylene jacket in conformance with ASTM D1248.  Color shall be blue.

- Tracer wires shall be connected together using moisture displacement connectors with strain relief.

- Schedule 80 PVC fittings shall meet the following requirements.

- Schedule 80 PVC fittings shall conform to ASTM D2467.

- PVC shall meet the requirement of Cell Classification 12454 in conformance with ASTM D1784.

E. Copper Pipe

  - Copper pipe shall meet the following requirements.

- Copper pipe shall conform to Federal Specifications WW-P-377 and ASTM B42 and ASTM B302.

- Copper pipe shall have plain ends and lengths standardized at 12 feet.

F. Copper Tubing

- Copper tubing shall meet the following requirements.

- Copper tubing shall be Type K, seamless copper tubing conforming to ASTM B88.

- Copper tubing may be used in 20-foot straight lengths or 60-foot/100-foot coils.

G. Steel Casing Pipe

- Steel casing pipe shall be new, seamless steel pipe conforming to ASTM A252, Grade 2.

- Minimum thickness shall be ¼-inch.

- Minimum tensile strength shall be 60,000 PSI.

- Minimum yield strength shall be 35,000 PSI.

- Minimum elongation in 2-inches shall be 25-percent.

- Steel casing pipe shall be coated on the interior and exterior with bituminous asphalt.

H. Casing Spacers

- Panel and riser shall be Type 304 stainless steel, cross-linked epoxy coated carbon steel, or thermoplastic powder coated carbon steel.

- Liner shall be elastomeric PVC, 0.09 inches thick, with a Durometer “Shore A” hardness of 85-90 and a minimum 58,000 volt dielectric strength in accordance with ASTM D149.

- Runners shall be glass reinforced polymer (nylon).

- Acceptable Manufacturers

- Advanced Products & Systems, Inc., Model SSI or Model SI

- Pipeline Seal and Insulator, Inc., Model S or Model C

- Power Seal Corporation, Model 4810

- City of Roswell Approved Equal

I. Polyethylene Encasement

- Where indicated on the Drawings, the Contractor shall provide a polyethylene encasement over pipe, fittings and valves.

- Ductile iron pipe that crosses or runs parallel to a gas transmission main, which is or may be cathodically protected, shall be encased in polyethylene tubing.

- Polyethylene encasement material shall be minimum 8-mil, low density, flat tube, virgin polyethylene film conforming to ANSI/AWWA C105/A21.5.

- Polyethylene encasement shall have the following properties.

- Tensile Strength: Minimum 3,600 PSI

- Elongation: Minimum 800%

- Dielectric Strength: Minimum 800 V/mil

- Impact Resistance: Minimum 600 grams

- Propagation Tear Resistance: Minimum 2,550 grams force

- Securing tape shall be 2-inch wide PVC pipe tape, minimum 10-mil thickness, 245-percent elongation, and 30 PSI tensile strength.

J. Water Main Valves

- General

- Valves 16-inches and smaller shall be gate valves.

- Valves 18-inches and larger shall be butterfly valves.

- Valves shall be placed at the intersection of all water mains.

- Valves shall be spaced at maximum 500 foot intervals in commercial districts and maximum 800 foot intervals in other districts.

- Gate valves 3-inches and smaller shall meet the following requirements.

- Gate valve shall be 200 PSI Cold Working Pressure, brass body, non-rising stem, full port valves conforming to Federal Specification WW-V-54D, Class A, Type 1.

- Gate valve shall be NSF/ANSI Standard 61 compliant.

- Gate valves 4-inches through 16-inches in size shall meet the following requirements.

- Resilient seated gate valve for water supply service conforming to AWWA C509.

- Valve body and bonnet shall be ASTM A126, Class B ductile iron.

- Disc shall be cast iron.

- Valve stem shall be cast bronze.

- Minimum 200 PSI working pressure.

- Buried valves shall have non-rising stem (NRS) operators with 2-inch operating nuts.

- Above grade (non-buried) valves shall have outside stem and yoke (OS&Y) operators.

- Gate valve shall open counterclockwise (left).

- Buried valves shall have MJ x MJ end connections.

- Above grade (non-buried) valves shall have FLG x FLG end connections.

- Interior and exterior surfaces shall be coated with fusion-bonded epoxy coating in conformance with AWWA C550.

- Gate valve shall be NSF/ANSI Standard 61 compliant.

- Acceptable Manufacturers

    - Dresser

    - M&H

    - Mueller

    - City of Roswell Approved Equal

- Butterfly valves shall meet the following requirements.

- Resilient seated butterfly valve conforming to AWWA C504.

- Valve body shall be ASTM A126, Class B ductile iron.

- Valve disc shall be ASTM A126, Class B ductile iron with Type 316 stainless steel edge.

- Valve stem shall be Type 304 stainless steel conforming to ASTM A276.

- Minimum 200 PSI working pressure.

- Buried valves shall have geared operator with 2-inch operating nut.

- Above grade (non-buried) valves shall have geared operator with hand wheel.

- Butterfly valve shall open counterclockwise (left).

- Buried valves shall have MJ x MJ end connections.

- Above grade (non-buried) valves shall have FLG x FLG end connections.

- Interior and exterior surfaces shall be coated with fusion-bonded epoxy coating in conformance with AWWA C550.

- Butterfly valve shall be NSF/ANSI Standard 61 compliant.

- Acceptable Manufacturers

    - BIF Industries

    - Dresser

    - Henry Pratt Company

    - City of Roswell Approved Equal

K. Combination Air/Vacuum Release Valves

- Combination Air/Vacuum (CAV) valves shall have a cast iron body, cover, and baffle, stainless steel float, bronze water diffuser and Buna-N seat with threaded fittings.

- Acceptable Manufacturers

- APCO Valve and Primer Company

- Crispin Valve

- GA Industries

- City of Roswell Approved Equal

L. Corporation Stops

- Corporation stops shall meet the following requirements.

- Brass corporation stops shall be low lead or lead free and shall conform to AWWA C800.

- ¾-inch and 1-inch corporation stop connections shall be AWWA/CC Taper Thread inlet x Pack Joint Copper Tube Size (CTS) Compression outlet or AWWA/CC Taper Thread inlet x Female Iron Pipe (FIP) Thread outlet.

- 1½-inch and 2-inch corporation stop connections shall be Male Iron Pipe (MIP) Thread inlet x Female Iron Pipe (FIP) Thread outlet.

- Acceptable Manufacturers

- Cambridge Brass (Hays)

- The Ford Meter Box Company, Inc.

- Mueller Co.

- City of Roswell Approved Equal

M. Curb Stops

- Brass curb stops shall be low lead or lead free and shall conform to AWWA C800.

- Curb stop connections shall be Pack Joint Copper Tube Size (CTS) Compression inlet x Pack Joint Copper Tube Size (CTS) Compression outlet or Pack Joint Copper Tube Size (CTS) Compression inlet x Female Iron Pipe (FIP) Thread outlet.

- Acceptable Manufacturers

- Cambridge Brass (Hays)

- The Ford Meter Box Company, Inc.

- Mueller Co.

- City of Roswell Approved Equal

N. Adapters and Unions

- Adapters and unions for copper tubing and pipe shall be low lead or lead free and shall conform to AWWA C800.

- Acceptable Manufacturers

- Cambridge Brass (Hays)

- The Ford Meter Box Company, Inc.

- Mueller Co.

- City of Roswell Approved Equal

O. Service Saddles

- Service saddles shall meet the following requirements.

- Double strap service saddles conforming to AWWA C800.

- Ductile iron body conforming to ASTM A536.

- AWWA/CC Taper Thread or Female Iron Pipe (FIP) Thread.

- Carbon steel straps conforming to ASTM A108.

- Nuts shall be heavy hex type, low carbon steel, zinc plated conforming to ASTM A563 and washers shall be SAE flat washers, low carbon steel, zinc plated conforming to ASTM F844.

- Fusion bonded epoxy coating conforming to AWWA C213.

- Heavy duty, Buna N outlet gasket.

- Service saddle shall be NSF/ANSI Standard 61 compliant.

- Acceptable Manufacturers

- The Ford Meter Box Company, Inc. Style F202

- Smith-Blair Style 313

- City of Roswell Approved Equal

P. Tapping Sleeves

- Tapping sleeves shall meet the following requirements.

- Ductile iron mechanical joint tapping sleeve.

- Minimum 200 PSI working pressure.

- Minimum tap size shall be 6”.

- Tapping sleeve shall have ¾” NPT test plug.

- Tapping sleeve shall be NSF/ANSI Standard 61 compliant.

- Acceptable Manufacturers

- M & H Model 2174

- Mueller Model H-615

- City of Roswell Approved Equal

Q. Steel Couplings

- Steel couplings shall meet the following requirements.

- Bolted, sleeve-type steel couplings shall conform to AWWA C219.

- Minimum 150 PSI working pressure.

- Coupling sleeve shall be carbon steel with a minimum yield of 30,000 PSI.

- Follower flanges shall be carbon steel or ductile iron.

- Hardware shall be heavy hex type, low carbon steel, zinc plated bolts conforming to ASTM A307, Grade B and heavy hex type, low carbon steel, zinc plated nuts conforming to ASTM A563, Grade B.

- Gaskets shall be Buna-N rubber.

- Steel couplings shall have fusion bonded epoxy coating conforming to AWWA C213.

- Steel couplings shall be NSF/ANSI Standard 61 compliant.

- Acceptable Manufacturers

- Dresser Manufacturing Company Style No. 38

- Smith-Blair Catalog No. 411

- City of Roswell Approved Equal

R. Blow-Off Station

- Blow-off station shall have 2-inch blow off valve and 3/8-inch sample port.

- Blow-off station shall have mechanical thermal control valve for freeze protection.

- Blow-off station shall be Hydro-Guard Safety-Guard BSS-02 BOSS Sample Station Model No. BSS-02-DIV-TCV.

S. Automatic Flushing System

- Automatic flushing system shall have nine event battery powered programmer, RPZ backflow prevention, 2-inch nylon glass reinforced valve, self draining double check valve, and sampling capabilities.

- Automatic flushing system shall have mechanical thermal control valve for freeze protection.

- Automatic flushing system shall be Hydro-Guard High Profile Flushing System Model No. HG-5-RPZ-8021-TCV.

T. Backflow Preventers

- Dual Check Backflow Preventer

- Brass dual check backflow preventer shall conform to AWWA C800 and shall be ASSE 1024 approved.

- Brass dual check backflow preventer shall have a maximum working pressure of 175 PSI.

- Acceptable Manufacturers

- The Ford Meter Box Company, Inc.

- City of Roswell Approved Equal

- Double Check Backflow Preventer

- Double check backflow preventer shall conform to ASTM C510.

- Acceptable Manufacturers

    - ¾” to 2” Double Check Backflow Preventers

      - Conbraco Model 40-104-A4T (¾”); 40-105-A4T (1”); 40-107-A4T (1½”); 40-108-A4T (2”)

      - Flowmatic Model B9100U (¾”); B9101U (1”)

      - Hersey Model FDC (all sizes)

      - Watts Model U-007QT-T-Z3 (all sizes)

      - Wilkins Model 950XLU (all sizes)

- 3” to 10” Double Check Backflow Preventers

- Ames Model 2000DCA/2000SE (8”)

- Conbraco Model 40-100 (3”)/10A (4”)/10C (6”)/10E (8”)/10G (10”)-03

- Febco Model 805YD-OS&Y-RW

- Hersey No. 2

- Watts Model 007/709/770-OS&Y-RW-A

- Wilkins Model 950-OS&Y

- Reduced Pressure Zone (RPZ) Backflow Preventer

- Reduced pressure zone (RPZ) backflow preventer shall conform to ASTM C511.

- Acceptable Manufacturers

    - ¾” to 2” RPZ Backflow Preventers

      - Conbraco Series 40-200-02

      - Flowmatic B9200

      - Hersey FRP II with unions and T-handles

      - Watts U-009QT-Z3

      - Wilkins 975 XLUS

    - 3” to 10” RPZ Backflow Preventers

- Ames Model 4000RP

- Conbraco Series 40-200

- Febco Model 825YD-OS&Y-RW

- Hersey Model 6CM

- Watts Model 909-OS&Y-RW-A

- Wilkins Model 975-ROS&Y

U. Fire Hydrants

- Fire hydrants shall meet the following requirements.

- Six inch, dry barrel, fire hydrant conforming to AWWA C502.

- Minimum 250 PSI working pressure.

- Fire hydrant shall have 6” MJ base connection.

- Fire hydrant shall have 5¼” main valve.

- Valve seats shall be bronze to bronze.

- Fire hydrant shall have automatic drain that closes fully when the main valve is open.

- Fire hydrant shall have one (1) 4½” pumper nozzle and two (2) 2½” hose nozzles.  Nozzle threads shall be the standard adopted by the National Board of Fire Underwriters (NBFU).  Nozzles shall have caps with gaskets and shall be fitted with chains.

- Fire hydrant shall have 1½” National Standard pentagon operating nut that opens counterclockwise.

- Fire hydrant color shall be silver.

- Minimum depth of bury shall be 4 feet.

- Acceptable Manufacturers

- M&H Model 129

- Mueller Super Centurion 250

- U.S. Pipe Model M94

V. Cast Iron Valve Boxes for Water Main Valves

- Valve boxes shall be cast-iron two or three piece with cast iron covers.

- The barrel shall be one or two-piece, screw type, having 5-1/4-inch shaft.

- Covers shall have “WATER” cast into the lid.

W. Valve Boxes for Service Line Valves

- Valve boxes for service line valves shall be high density polyethylene or fiber reinforced plastic.

- Valve boxes shall be minimum 6” diameter by 9” tall boxes with T-cover.

- Valve box color shall be black.

- Acceptable Manufacturers

- Carson/Oldcastle Precast, Inc.

- DFW Plastics, Inc.

- City of Roswell Approved Equal

X. Water Meter Boxes

- ¾” Meters

- Water meter boxes for ¾” water meters shall be Ford Meter Box Company, Inc. Long Yoke box Model LYLB 141-233-ROS-T with locking lid and 2” meter read hole.

- 1” and Larger Meters

- Water meter boxes for 1” and larger water meters shall be high density polyethylene or fiber reinforced plastic.

- Water meter box lids shall be cast iron T-cover with 2” diameter hole offset for touch read installation.

- Acceptable Manufacturers

    - Carson/Oldcastle Precast Inc. Specification Grade 1220-12

    - DFW Plastics, Inc. 1500.12.1

Y. Meter Vaults and Valve Vaults

- Meter vaults and valve vaults shall be precast concrete in accordance with ASTM C478.

- Concrete compressive strength shall be 4,000 PSI at 28 days.

- Tongue and groove joints with preformed butyl joint seals.

- Minimum 48”x48” double door, aluminum access hatch.  Access hatch shall be rated for 300 PSF, shall be hinged with tamper proof bolts, shall have automatic hold open arm, shall have flush aluminum drop handle, and shall have staple for pad lock.  All hardware shall be Type 316 stainless steel.

- Steps shall be copolymer polypropylene type with ½” Grade 60 steel reinforcing conforming to ASTM C478.

- Steps shall be located at hatch and hatch shall be offset so that steps are accessible.

4.3	Execution

- Care shall be taken in loading, transporting and unloading to prevent damage to the pipe or coatings.  Pipe and fittings shall not be dropped.  All pipe or fittings shall be examined before installation, and no piece shall be installed which is found to be defective.  Any damage to the pipe coatings shall be repaired as directed by the City of Roswell.

- Pipe and fittings shall be subjected to a careful inspection just prior to being laid or installed.  If any defective pipe is discovered after it has been laid it shall be removed and replaced with a sound pipe in a satisfactory manner at no additional expense to the City of Roswell.  All pipe and fittings shall be thoroughly cleaned before laying, shall be kept clean until they are used in the work, and when installed or laid, shall conform to the lines and grades required.

- Unless specifically indicated otherwise, underground piping shall slope uniformly between joints.

- Contractor shall exercise extreme care when constructing piping to protect from damage all existing underground utilities, and all existing structures.

4.3.1	Installation

- General

  - Pipe and fittings shall be installed using bedding, as shown on the drawings, and in accordance with requirements of AWWA except as otherwise provided herein.  A firm, even bearing throughout the length of the pipe shall be constructed by tamping selected material at the sides of the pipe up to the spring-line.  BLOCKING SUPPORTS WILL NOT BE PERMITTED.  Bell holes shall be hand excavated to insure uniform bearing along the pipe barrel.

  - All pipe shall be sound and clean before laying.  When pipe laying is not in progress, including lunchtime, the open ends of the pipe shall be closed by watertight plug or other approved means.  Good alignment shall be preserved in laying.  The deflection at joints shall not exceed that recommended by manufacturer.

  - When cutting pipe is required, the cutting shall be done by machine, leaving a smooth cut at right angles to the axis of the pipe.  Cut ends of pipe to be used with a bell shall be beveled to conform to the manufactured spigot end.  Lining shall be undamaged.

  - Push-on joints shall be made in strict accordance with the manufacturer's instructions.  Pipe shall be laid with bell ends looking ahead.  A rubber gasket shall be inserted in the groove of the bell end of the pipe, and the joint surfaces cleaned and lubricated.  The plain end of the pipe is to be aligned with the bell of the pipe to which it is to be joined, and pushed home with a jack or by other means.  After joining the pipe, a metal feeler shall be used to make certain that the rubber gasket is correctly located.

  - Joints at fittings, and where designated on the drawings and/or as specified, shall be in accordance with the "Notes on Method of Installation” in ANSI/AWWA C111/A21.11 and the instructions of the manufacturer.  To assemble the joints in the field, thoroughly clean the joint surfaces and rubber gasket with soapy water before assembly.

  - Unless otherwise noted, underground piping shall be push-on joint.

  - All fittings and other appurtenances needed upon the pipe lines shall be set and jointed as indicated on the Drawings or as required by the manufacturer.

  - If requested, the Contractor shall arrange for the pipe manufacturer to furnish information and supervise the installation of at least the first five (5) push-on joints.

  - The Contractor shall carefully regulate his equipment and construction operations such that the loading of the pipe does not exceed the loads for which the pipe is designed and manufactured.  Any pipe damaged during construction operations shall be replaced at the Contractor's expense.

  - All piping shall be properly and adequately supported.  Supports shall be provided as indicated on the Drawings.  If the method of support is not indicated on the Drawings, piping shall be supported as directed by the City of Roswell.

  - The proper number of gaskets and all necessary joint materials, plus one extra gasket for every 50 joints or fraction thereof, shall be furnished with the pipe and fittings.

  - Pipe embedment shall conform to manufacturer's recommendations.  Bedding and backfill for pipe shall be as shown on the Drawings.

  - All “Dead End” Lines shall have a blow-off station, flushing station, or hydrant installed on the end for flushing purposes, or equivalent.

B. Pipe Supports and Thrust Blocks

- All piping shall be properly and adequately supported.  Concrete piers and pads shall be provided as indicated on the Drawings.  If the method of support is not indicated on the Drawings, exposed piping shall be supported as directed by the City of Roswell.

- All fittings shall have two forms or restraint (i.e. thrust block and restrained joint glands; restrained joint glands and threaded rods; thrust block and threaded rods).

- Longitudinal thrust along pressurized pipelines at bends, tees, reducers, and caps or plugs shall be counteracted by enough weight of concrete to counterbalance the vertical and horizontal thrust forces.

- Pipe and fittings shall be protected by a minimum 10-mil plastic sheet prior to placing concrete thrust block.

- Bearing area of thrust blocks shall be adequate to prevent any movement of the fitting and shall be of the size and dimensions as shown on the Drawings.

- Concrete for thrust blocking shall be minimum 3000 PSI.  Concrete shall be placed against undisturbed material, and shall not cover joints, bolts or nuts, or interfere with the removal of any joint.  Wooden side forms shall be provided for thrust blocks.

- Restrained joints shall be used as shown on the Drawings.  Thrust blocks shall be used at all other locations or as directed by the City of Roswell.

- All thrust blocking shall be inspected by the City of Rowell prior to the thrust block being buried.

C. Pressure and Leakage Tests of Underground Pressure Piping

- Hydrostatic pressure and leakage tests shall conform to Section 4 of ANSI/AWWA C600 with the exception that the Contractor shall furnish all gauges, meters, pressure pumps and other equipment needed to test the line.  The pressure gauge used for testing shall be laboratory calibrated suitable for the test pressure required.

- The pressure required for the field hydrostatic pressure test shall be 150% of the maximum operating pressure of the section, or the pressure class of the pipe, whichever is greater.  The Contractor shall provide temporary plugs and blocking necessary to maintain the required test pressure.  Corporation cocks at least ¾-inches in diameter, pipe riser and angle globe valves shall be provided at each pipe dead-end and high point in order to bleed air from the line.  Duration of pressure test shall be at least 2 hours.  The cost of these items shall be included as a part of testing.

- The contractor shall contact the City of Roswell prior to conducting any pressure test.  A record of successful pressure testing results will be provided by the contractor to the City of Roswell inspector at the time of observing the leakage testing.

- The leakage test shall be a separate test at the maximum operating pressure as determined by the City of Roswell following the pressure test and shall be of not less than 2 hours duration.  All exposed pipes, fittings, valves and joints will be carefully examined during the tests and all leaks evident at the surface shall be repaired and leakage eliminated regardless of total leakage as shown by test.  Lines that fail to meet tests shall be repaired and retested as necessary until test requirements are complied with.  Defective materials, pipes, valves and accessories shall be removed and replaced.  The pipe lines shall be tested in such sections as may be directed by the City of Roswell by shutting valves or installing temporary plugs as required.  The line shall be filled with water and all air removed and the test pressure shall be maintained in the pipe for the entire test period by means of a force pump to be furnished by the Contractor.  Accurate means shall be provided for measuring the water required to maintain this pressure.  The amount of water required is a measure of the leakage.

- The amount of leakage that will be permitted shall be in accordance with AWWA C600 Standards for all pressure lines.  No pipe installation will be accepted if the leakage is greater than that determined by the following formula:

L=SDP133,200

Where:

L = Testing Allowance (Makeup Water), GPH

S = Length of Pipe Tested, ft

D = Nominal Diameter of Pipe, in

P = Test Pressure, PSIG

- The Contractor may backfill the trench before he tests the line if he so desires, but he shall open up the trench at his own expense to repair any leaks.

- The Contractor must submit his plan for testing to the City of Roswell for review at least three (3) days before starting the test.  The Contractor shall remove and adequately dispose of all temporary blocking material and equipment after completion and acceptance of the field hydrostatic test, unless otherwise directed by the City of Roswell.  The Contractor shall repair any damage to the pipe coating.  Lines shall be totally free and clean prior to final acceptance.

D. Cleaning Mains

- At the conclusion of the Work, the Contractor shall thoroughly clean the new pipeline by flushing with water or other means to remove all dirt, stones, and pieces of wood or other material that may have entered during the construction period.  If, after this cleaning, obstructions remain they shall be removed.

E. Disinfection

- Upon completion of the pressure and leakage test, the section of pipe to be disinfected shall be initially flushed using potable water.  Flushing shall be accomplished at a minimum velocity of 2.5 feet per second and shall continue until the water runs clear.

- Disinfection shall be accomplished by the continuous feed chlorination method in accordance with ANSI/AWWA C651.  The following steps shall be employed:

    - Begin filling main at a constant, measured rate with potable water.  As water first flows in, begin adding chlorine at a point no more than ten feet from the beginning of the new main.

    - Add chlorine at a rate to attain a 50 mg/l chlorine concentration.  The acceptable method is by preparing a 1% solution with sodium hypochlorite or calcium hypochlorite.

    - Continue adding chlorine at a rate to attain a minimum concentration of 50 mg/l.  Measure the rate at regular intervals as given in AWWA M12 or with a high range test kit.  Chlorine application shall continue until the entire main is filled.

    - The chlorinated water shall be retained in the water main for a minimum of 24 hours.  At the end of the 24-hour period the water in all portions of the main shall have a minimum chlorine residual of 10 mg/l.

    - The heavily chlorinated water shall be flushed in a manner that is not detrimental to the environment.  The method proposed shall be submitted to and approved by the City of Roswell prior to discharge.  Final flushing shall continue until the chlorine residual is less than 1 mg/l.

    - Contractor shall coordinate sampling with the City of Roswell.  No earlier than 16 hours after final flushing, the City of Roswell will obtain bacteriological samples for testing.

    - If bacteriological test results are unsatisfactory, the Contractor shall either flush the main with potable water or re-disinfected, as directed by the City of Roswell, prior to obtaining additional samples.  Satisfactory bacteriological test results shall be obtained prior to placing the new main in service or prior to a final plat approval on which a new water service has been constructed.

F. Separation of Water and Sewer Lines

- There shall be no physical connection between a drinking water supply line and a sewer or appurtenance.

- Water lines shall be laid at least ten (10) feet horizontally from a sewer or a sewer manhole whenever possible; the distance shall be measures edge-to-edge.  When local conditions prevent a horizontal separation of ten (10) feet, the water line may be laid closer to a sewer or sewer manhole provided that:

- The bottom (invert) of the water main shall be at least eighteen (18) inches above the top (crown) of the sewer

- Where this vertical separation cannot be obtained, the sewer shall be constructed of ductile iron pipe and pressure tested in place without leakage prior to backfilling.

- The water line shall be laid in separate trenches or on an undisturbed earth shelf.

- Where possible the water main shall pass over the sewer main with a vertical separation of at least eighteen (18) inches.  When local conditions prevent a vertical separation of eighteen (18) inches between the bottom of the water main and the top of the sewer the following construction standards shall be used:

- The sewer shall be constructed of ductile iron pipe and pressure tested in place without leakage prior to backfilling.

- Adequate structural support for both the water and sewer mains shall be provided to prevent settling and excessive deflection of the joints.

- That length of sewer main shall be centered at the point of the crossing such that the joints shall be equidistant from the point of crossing.

- No deflection of the joints is permitted within ten (10) feet of the point of crossing.

G. Repair and Replacement

- Any cracked or broken material, such as pipe, fittings, valves, or hydrants, shall be removed and replaced with sound pieces.  Joints that leak shall be carefully remade.  Remade joints and replaced material shall be re-tested under the same conditions of operation.  If joints or materials are then found to be defective, they shall be remade and replaced until the line passes the required test.

- Upon completion of back-filling and consolidation of the back-fill, all pavements removed for construction of the pipelines and appurtenance shall be replaced also and all pavements adjacent to pipe trenches, which may have been disturbed or damaged as the result of construction operations shall be removed and replaced and a load test conducted to prove proper consolidation of back-fill to sustain a load of 2500 pounds per square foot without undue settlement.  Replacement shall be in accordance with the regulations of the Georgia Department of Transportation (GDOT) and the City of Roswell.

- Pavement, including driveways, shall be replaced to a minimum width of nine inches beyond the top edges of each side of the trench excavation to allow solid bearing and to the depth as follows:

- Concrete pavement shall be replaced with a minimum depth of eight inches of concrete having a minimum compressive strength of 3,000 psi in 28 days.

- Asphalt paving shall be replaced with an 8-inch concrete cap and 1½-inches of Type “F” asphalt paving.

- For street cuts greater than 150 feet in length, the entire width of the roadway shall be overlaid with 1½-inches of Type “F” asphalt paving.  When directed by the City of Roswell, the entire street width shall be milled 1½-inches prior to placing the surface course.

- Driveways and sidewalks shall be replaced with in-kind material.

4.4	Water Mains and Fire Hydrants on Private Property and Subdivision Developments

- Water mains of at least eight-inch pipe shall be installed; six-inch pipe may be used only where it completes a gridiron and then only up to 600 feet in length between interconnecting mains of approved diameter, unless otherwise approved by the Director of Public Works and the Fire Marshal.  All pipe materials shall comply with the standards approved by the City of Roswell.

- No main line smaller than eight inches shall serve more than one fire hydrant and automatic extinguishing system or one fire hydrant on any dead-end main more than 500 feet in length.  All water mains shall be sized in accordance with NFPA 24, as adopted by the State of Georgia.

- Fire hydrants shall be spaced not more than 500 feet apart, with additional fire hydrants located as necessary to Comply with the requirements of the International Fire Code and Appendices as adopted by the City of Roswell and approved by the Fire Marshal.

- Water mains shall be of ductile iron or copper or a type listed for this service by a nationally recognized testing laboratory.  They shall be installed at least 30 inches below grade and shall be tested hydrostatically at not less than 200-psi pressure for two hours in the presence of a representative of the city.

- Hydrants, fittings, valves and Fire Department connections shall be approved by the Fire Department.  Fire Department connections shall be not less than 18 inches or more than 36 inches above the level of the adjoining ground or paving.  The thread of such connections shall be uniform with that used by the Fire Department.

- Water mains and fire hydrants shall be installed, under water pressure and ready for fire fighting before any construction with combustible material begins on-site.